Memo:
計算式のmmlファイルへの保存：計算式ボックスを左クリックで選択　→　右クリック　→　「名前を付けてコピーを保存」　→　「MathML 2.0」を選択

NTU method
Parallel flow heat exchanger
ε: heat exchanger effectiveness newline Q_{max,theoretical}:heat exchanged, theoretically max newline dm: mass flow rate newline Cp: specific heat newline C_{ min }: heat capacity flow, minimum side newline C_max{ max }: heat capacity flow, max side newline Cr: heat capacity ratio newline NTU: Number of thermal unit newline ( UA ): overall heat conductance newline T_hi: hot side fluid temperature newline T_ci: cold side fluid temperature newline h_h: hot side convection coefficient newline h_c: cold side convectin coefficient newline A_h: hot side heat transfer area newline A_c: cold side heat transfer area

{ ε} = {Q_actual} over { Q_{max,potential} } newline Q_max= C_min * ( T_hi - T_ci )

ε= {1-exp [-NTU* (1-Cr)] } over {1-Cr*exp[-NTU*(1-Cr)]} (for c<1) newline ε= {NTU} over {1+NTU} (for c=1) newline Cr= {C_min} over {C_max} newline NTU= { (UA) } over {C_min} newline C_min=min ( lbrace dm*Cp rbrace_{hot,inlet},lbrace dm*Cp rbrace_{cold,inlet} ) newline C_max=max ( lbrace dm*Cp rbrace_{hot,inlet},lbrace dm*Cp rbrace_{cold,inlet} ) newline {1} over {(UA)}= {1} over {h_h *A_h} + {1} over {h_c * A_c} newline "* heat conduction of wall is ignored in this equation above"